## Wirefill
Wiring Trunking Size Calculator |  |  |  |  | Suitable Duct Sizes |  |  |  | Derating Factor | Percentage | Size
Wire | Quantity | O.D. | Total |  | Width (mm) | Height (mm) | Area (mm) | Size | 0.1 | 5% | 15
0.5 | 1 | 2.5 | 2.5 |  | 15 | 15 | 225 | TOO SMALL | 0.2 | 10% | 25
0.75 |  | 2.7 | 0 |  | 15 | 25 | 375 | TOO SMALL | 0.3 | 15% | 37.5
1 | 15 | 2.95 | 44.25 |  | 15 | 40 | 600 | OK | 0.4 | 20% | 40
1.5 |  | 3.2 | 0 |  | 25 | 25 | 625 | OK | 0.5 | 25% | 50
2.5 | 6 | 3.65 | 21.9 |  | 25 | 37.5 | 937.5 | OK | 0.6 | 30% | 60
4 | 3 | 4.2 | 12.6 |  | 25 | 40 | 1000 | OK | 0.7 | 35% | 75
6 |  | 4.7 | 0 |  | 25 | 50 | 1250 | OK | 0.8 | 40% | 80
10 |  | 6.5 | 0 |  | 25 | 75 | 1875 | OK | 0.9 | 45% | 100
16 |  | 8 | 0 |  | 37.5 | 37.5 | 1406.25 | OK | 1 | 50% | 120
25 |  | 9.4 | 0 |  | 37.5 | 50 | 1875 | OK |  | 55% | 150
35 |  | 10.6 | 0 |  | 40 | 25 | 1000 | OK |  | 60%
50 |  | 12.9 | 0 |  | 40 | 40 | 1600 | OK |  | 65%
70 |  | 14.6 | 0 |  | 40 | 60 | 2400 | OK |  | 70%
95 |  | 16.1 | 0 |  | 40 | 80 | 3200 | OK |  | 75%
<<enter>> |  |  | 0 |  | 40 | 100 | 4000 | OK |  | 80%
<<enter>> |  |  | 0 |  | 50 | 37.5 | 1875 | OK |  | 85%
<<enter>> |  |  | 0 |  | 50 | 50 | 2500 | OK |  | 90%
<<enter>> |  |  | 0 |  | 50 | 75 | 3750 | OK |  | 95%
<<enter>> |  |  | 0 |  | 60 | 40 | 2400 | OK |  | 100%
<<enter>> |  |  | 0 |  | 60 | 60 | 3600 | OK |  | 100%
<<enter>> |  |  | 0 |  | 60 | 80 | 4800 | OK |  | 100%
<<enter>> |  |  | 0 |  | 60 | 100 | 6000 | OK
<<enter>> |  |  | 0 |  | 75 | 50 | 3750 | OK
<<enter>> |  |  | 0 |  | 75 | 75 | 5625 | OK
<<enter>> |  |  | 0 |  | 80 | 40 | 3200 | OK
<<enter>> |  |  | 0 |  | 80 | 60 | 4800 | OK
<<enter>> |  |  | 0 |  | 80 | 80 | 6400 | OK
<<enter>> |  |  | 0 |  | 80 | 100 | 8000 | OK
<<enter>> |  |  | 0 |  | 100 | 40 | 4000 | OK
<<enter>> |  |  | 0 |  | 100 | 60 | 6000 | OK
<<enter>> |  |  | 0 |  | 100 | 80 | 8000 | OK
<<enter>> |  |  | 0 |  | 100 | 100 | 10000 | OK
<<enter>> |  |  | 0 |  | 120 | 100 | 12000 | OK
<<enter>> |  |  | 0 |  | 150 | 100 | 15000 | OK
Average Wire O.D. Calculation |  |  |  | Wirefill Calculator
Summary of No. Wires x O.D. |  |  | 81.25 | Choose Width (mm) |  |  |  | 40
Total No. Wires |  |  | 25 | Choose Height (mm) |  |  |  | 40
Average O.D. |  |  | 3.25 | Required fill factor (%PD) |  |  |  | 0.5
|  |  |  | Twist/Air Derating Factor (DF) |  |  |  | 0.9
|  |  |  | Total Area (((No. wires x πr²)/DF)/%PD) |  |  |  | 460.9358
|  |  |  | Maximum Average O.D. Wires Allowed |  |  |  | 86.78
((WxHx%PD/πr²)xDF)
|  |  |  | Actual fill factor % (Total area/(WxH)) |  |  |  | 28.81%
Tri-rated cable specifications in accordance with BS6231 defined by Eland Cables / Duct sizes defined by Legrand
Cadline assume no responsibility for the accuracy of the above information